POLAR GRID

AI-Assisted Renewable Energy Forecasting & Microgrid Dispatch Optimization for Antarctic Stations

Project Type: College SIH Prototype / Operational Decision-Support System

Target Case Study: Mawson Station, Mac. Robertson Land, Antarctica (67.6027° S, 62.8738° E)

Key Value Proposition: Reduces expensive, high-emission diesel generator fuel consumption by forecasting renewable surges (wind and solar), buffering with battery energy storage (BESS), and optimizing microgrid dispatch using Linear Programming.

_________________________________________________________________________________

1. WHAT IS POLAR GRID?

Polar Grid is an intelligent microgrid decision-support system designed for Antarctic research stations. It forecasts upcoming ambient weather and station electrical demand for the next 24 to 72 hours, estimates renewable power from installed solar panels and wind turbines, and computes an hourly generator and battery dispatch schedule that minimizes diesel fuel consumption while guaranteeing power reliability.

_________________________________________________________________________________

2. WHAT DATA DO WE USE?

Polar Grid uses two authentic sources of data:

1. Station Energy Data: Official monthly records from the Australian Antarctic Data Centre (AADC):

⁃ indicator_59.csv: 30 years of historical monthly Mawson electricity consumption (1986–2016, 360 records).

⁃ indicator_56.csv: 23 years of historical monthly generator and boiler diesel fuel consumption (1993–2016, 278 records).

2. Atmospheric Weather Data: Genuine hourly reanalysis from the ECMWF ERA5 atmospheric reanalysis for Mawson Station coordinates (-67.6027°S, 62.8738°E), covering:

⁃ 2-metre air temperature (°C)

⁃ 10-metre wind velocity (m/s) and direction

⁃ Surface solar irradiance (W/m²) and direct/diffuse normal radiation

Demo Safety Note: All ERA5 and station data files are cached locally in `data/raw/` and `data/processed/`. The entire project runs 100% offline without needing an active internet connection.

_________________________________________________________________________________

3. WHAT IS REAL VS MODELED? (DATA TRANSPARENCY)

Polar Grid maintains strict scientific honesty:

• REAL HISTORICAL DATA:

⁃ 30 years of historical monthly Mawson electricity consumption records (AADC).

⁃ 23 years of historical monthly generator diesel fuel consumption records (AADC).

⁃ Hourly atmospheric weather parameters from ECMWF ERA5 reanalysis.

• MODELED DATA:

⁃ Hourly Station Electrical Load: The supplied historical station dataset provides monthly aggregates (~135,000 kWh/month) rather than hourly telemetry. We model the hourly demand curve using physical Antarctic heating degree-hours plus diurnal station activity, strictly calibrated so that its monthly total matches the real historical Mawson electricity consumption (average load ~185 kW continuous). Real hourly station electricity telemetry would improve the final system.

⁃ Solar PV Generation: Modeled from solar irradiance, ambient temperature, panel efficiency, and inverter ratings.

⁃ Wind Turbine Generation: Modeled from wind speed using the physical piecewise power curve of Mawson's actual 100 kW Antarctic-grade turbines.

• FORECASTED DATA:

⁃ 1-hour-ahead rolling predictions produced by Gradient Boosting models trained with chronological train/test splits.

• SIMULATED DISPATCH SAVINGS:

⁃ Fuel reduction figures represent mathematical dispatch optimization comparisons against a standard 100% diesel baseline under specific seasonal scenarios. They are simulated savings, not guaranteed annual contractual savings.

_________________________________________________________________________________

4. HOW DOES THE PIPELINE WORK?

Raw AADC Records + ERA5 Hourly Weather ↓ 1. Preprocessing & Data Cleaning (Filter Mawson, parse timestamps, interpolate missing values) ↓ 2. Calibrated Hourly Load Synthesis (Thermodynamic heating deficit + diurnal human activity, calibrated to real monthly totals) ↓ 3. Feature Engineering (Cyclical sin/cos hour, day-of-year, 1h/2h/24h lags, 6h/24h rolling averages) ↓ 4. ML Forecasting (Scikit-Learn HistGradientBoosting) (Chronological 80/20 train/test split, predicting demand, wind, solar, temperature) ↓ 5. Physical Renewable Estimation (Solar PV with cold air boost + 2x100kW wind turbines with cut-in/cut-out) ↓ 6. Linear Programming Optimization (SciPy linprog HiGHS) (Minimizes diesel fuel while enforcing power balance and 20%-95% battery SoC) ↓ 7. Baseline Comparison & Output Generation (Outputs schedule CSVs, impact metrics, and interactive dashboard)

_________________________________________________________________________________

5. HOW DOES THE OPTIMIZER WORK?

The dispatch scheduler uses Linear Programming (LP) solved with scipy.optimize.linprog using the HiGHS interior-point/simplex solver:

• Objective: Minimize total diesel fuel consumption ($F_{\text{diesel}}$) plus heavy penalty on unmet load.

• How it decides: For each future hour, Polar Grid decides how much energy should come from renewable sources, battery storage, and diesel while respecting physical system constraints:

1. Exact Power Balance: $\text{Generation (Renewables Used + Battery Discharge + Diesel)} = \text{Consumption (Demand + Battery Charge)}$.

2. Battery SoC Bounds: Battery energy must remain between $20.0\%$ and $95.0\%$ of its $300\text{ kWh}$ capacity to prevent degradation and freeze-damage.

3. Battery Continuity: Energy tracked with $90\%$ round-trip efficiency ($\eta_{\text{ch}} = \eta_{\text{dis}} \approx 94.87\%$).

4. Generator Limits: Diesel capacity capped at $375\text{ kW}$ ($3 \times 125\text{ kW}$ units).

_________________________________________________________________________________

6. HOW TO RUN THE PROJECT (WINDOWS)

Step 1: Run Unit Tests

python -m unittest discover -s tests -v

(All 5 test cases pass in ~0.10s)

Step 2: Run the Complete Master Pipeline

python run_pipeline.py

(Executes end-to-end in ~8.4 seconds and saves schedule CSVs and charts into `outputs/`)

Step 3: Launch the Full Application & Dashboard

uvicorn backend.main:app --host 127.0.0.1 --port 8000

Open your browser at: `http://127.0.0.1:8000/`

_________________________________________________________________________________

7. HOW TO DEMONSTRATE THE TWO SCENARIOS

Scenario A: Polar Summer (Late December)

1. In the dashboard top bar, select "☀️ Austral Summer (Dec • 24h Sun)".

2. What to show:

⁃ Continuous 24-hour solar daylight (solar generation peaks up to ~78 kW).

⁃ Strong Antarctic winds (~10 m/s) producing high clean energy.

⁃ Diesel reduction reaches ~78.6% over 48 hours.

⁃ The stacked area chart shows green (renewables) and purple (battery) supplying almost the entire station load, with red (diesel) running only during minor wind dips.

Scenario B: Polar Winter (July • Polar Night)

1. In the dashboard top bar, click "❄️ Polar Night (Jul • No Sun)".

2. What to show:

⁃ Complete polar night: Solar generation drops to exactly 0.0 kW.

⁃ The microgrid relies strictly on wind turbines, battery buffering, and diesel backup.

⁃ Diesel reduction is ~25.8% (powered by wind).

⁃ Shows that renewable microgrids still provide significant savings even in pitch-black Antarctic winter.

_________________________________________________________________________________

8. KNOWN LIMITATIONS

1. Monthly to Hourly Calibration: True station electricity consumption was recorded monthly. Hourly load was modeled from physical heating equations and calibrated to the monthly totals.

2. 1-Step Rolling Forecasting: The ML model predicts 1 hour ahead using the most recent true sensor observation ($t-1$). Over a full 48-hour open-loop horizon without sensor updates, prediction error would accumulate.

3. Seasonal Contrast: The ~78% diesel reduction is a peak summer result. Annual average diesel savings across all 12 months are projected at ~38%–45%.

_________________________________________________________________________________

9. PROJECT DOCUMENTATION

For detailed technical audits, test coverage, dataset specifications, and demo defense guides, check the docs/ directory:

• Validation Report

• Final MVP Status

• SIH Demo Guide

• SIH Jury Q&A Guide

• Test Report & Audit

• Testing Summary

• Dataset Report